Please make all changes in RED and include a justification.

Justification:

6.1 AC point

6.1.1 Introduction

The AC points may be implemented in several devices. All devices that report the generation or demand for AC power use the following formats to describe the AC power use at their input, output, or measurement point (see Table 6.1.1).

Table 6.1.1 — AC point definition

| Device attribute | Value |
| --- | --- |
| Category | Common DG format |
| Default Source Address | N/A |
| Dynamic Address Range | N/A |
| Instance | Multi-instance |

The DGs defined in the following clauses supply a common format to simplify the interpretation of AC information.

The instance field differs in interpretation according to the device type. The meaning of the instance field is defined within each device description.

Devices that support one AC_STATUS message are not required to support the others.

6.1.2 AC Point Status 1

Table 6.1.2a defines the DG attributes, and Table 6.1.2b defines the signal and parameter attributes.

Table 6.1.2a — DG definition

| DG attribute | Value |
| --- | --- |
| Name | AC_STATUS_1 |
| DGN | Defined in device specific definition |
| Default priority | Defined in device specific definition |
| Maximum broadcast gap | Defined in device specific definition |
| Normal broadcast gap | Defined in device specific definition |
| Minimum broadcast gap | 50 ms, see 3.2.4.2 |
| Number of frames | 1 |
| ACK requirements | N/A |

Table 6.1.2b — Signal and parameter definition

| Byte | Bit | Name | Data type | Unit | Value definition |
| --- | --- | --- | --- | --- | --- |
| 0 | - | Instance | uint8 | - | The interpretation depends on the device. |
| 1 to 2 | - | RMS voltage | uint16 | Vac | see Table 5.3 |
| 3 to 4 | - | RMS current | uint16 | Aac | see Table 5.3 |
| 5 to 6 | - | Frequency | uint16 | Hz | Precision = 1/128 Hz Value range = 0 to 500 Hz |
| 7 | 0 to 1 | Fault – open ground | uint2 | - | 00b — no fault 01b — open ground fault detected |
|  | 2 to 3 | Fault – open neutral | uint2 | - | 00b — no fault 01b — open neutral fault detected |
|  | 4 to 5 | Fault – reverse polarity | uint2 | - | 00b — no fault 01b — reverse polarity fault detected |
|  | 6 to 7 | Fault – ground current | uint2 | - | 00b — no fault 01b — ground current fault detected |

6.1.3 AC Point Status 2

Table 6.1.3a defines the DG attributes, and Table 6.1.3b defines the signal and parameter attributes.

Table 6.1.3a — DG definition

| DG attribute | Value |
| --- | --- |
| Name | AC_STATUS_2 |
| DGN | Defined in device specific definition |
| Default priority | Defined in device specific definition |
| Maximum broadcast gap | Defined in device specific definition |
| Normal broadcast gap | Defined in device specific definition |
| Minimum broadcast gap | 50 ms, see 3.2.4.2 |
| Number of frames | 1 |
| ACK requirements | N/A |

Table 6.1.3b — Signal and parameter definition

| Byte | Bit | Name | Data type | Unit | Value definition |
| --- | --- | --- | --- | --- | --- |
| 0 | - | Instance | uint8 | - | The interpretation depends on the device. |
| 1 to 2 | - | Peak voltage | uint16 | Vac | see Table 5.3 |
| 3 to 4 | - | Peak current | uint16 | Aac | see Table 5.3 |
| 5 to 6 | - | Ground current (High Range) | uint16 | Aac | see Table 5.3 |
| 7 | - | Capacity | uint8 | Aac | see Table 5.3 This generally shall indicate the size of the breaker on the circuit. In demand applications it may indicate the peak current requirements for the device. |

6.1.4 AC Point Status 3

Table 6.1.4a defines the DG attributes, and Table 6.1.4b defines the signal and parameter attributes.

Table 6.1.4a — DG definition

| DG attribute | Value |
| --- | --- |
| Name | AC_STATUS_3 |
| DGN | Defined in device specific definition |
| Default priority | Defined in device specific definition |
| Maximum broadcast gap | Defined in device specific definition |
| Normal broadcast gap | Defined in device specific definition |
| Minimum broadcast gap | 50 ms, see 3.2.4.2 |
| Number of frames | 1 |
| ACK requirements | N/A |

Table 6.1.4b — Signal and parameter definition

| Byte | Bit | Name | Data type | Unit | Value definition |
| --- | --- | --- | --- | --- | --- |
| 0 | - | Instance | uint8 | - | The interpretation depends on the device. |
| 1 | 0 to 1 | Waveform | uint2 | - | 00b — sine wave 01b — not a true sine wave This shall apply to inverters with “modified” or “quasi” sine wave outputs. |
|  | 2 to 5 | Phase status | uint4 | - | 0000b - No complementary leg 0001b - In phase (240 VAC not available) 0010b - 180 Degrees out of phase (240 VAC available) 0011b - Phase relationship is variable 1110b - Error 1111b - No data |
| 2 to 3 | - | Real power | uint16 | W | Precision = 1 W Value range = 0 to 65530 W |
| 4 to 5 | - | Reactive power | uint16 | VAr | Precision = 1 VAr Value range = -32000 to +33530 Var 0 = -32000 VAr, 32000 (7D00h) = 0 VAr Negative values are “lagging”, positive values are “leading”. |
| 6 | - | Harmonic distortion | uint8 | % | see Table 5.3 |
| 7 | - | Complementary Leg | uint8 | - | Instance of complementary leg (see Phase status [bytes 0 & 1 of this Table]) |

6.1.5 AC Point Status 4

Table 6.1.5a defines the DG attributes, and Table 6.1.5b defines the signal and parameter attributes.

Table 6.1.5a — DG definition

| DG attribute | Value |
| --- | --- |
| Name | AC_STATUS_4 |
| DGN | Defined in device specific definition |
| Default priority | Defined in device specific definition |
| Maximum broadcast gap | Defined in device specific definition |
| Normal broadcast gap | Defined in device specific definition |
| Minimum broadcast gap | 50 ms, see 3.2.4.2 |
| Number of frames | 1 |
| ACK requirements | N/A |

Table 6.1.5b — Signal and parameter definition

| Byte | Bit | Name | Data type | Unit | Value definition |
| --- | --- | --- | --- | --- | --- |
| 0 | - | Instance | uint8 | - | The interpretation depends on the device. |
| 1 | - | Voltage fault | uint8 | - | 0 - Voltage OK 1 - Extremely low voltage 2 - Low voltage 3 - High voltage 4 - Extremely high voltage 5 = Open Line 1 Detected 6 = Open Line 2 Detected |
| 2 | 0 to 1 | Fault – Surge protection | uint2 | - | 00b - No fault 01b - Surge fault detected (Service request for surge protector) |
|  | 2 to 3 | Fault – High frequency | uint2 | - | 00b - No fault 01b - Frequency over high limit |
|  | 4 to 5 | Fault – Low frequency | uint2 | - | 00b - No fault 01b - Frequency below low limit |
|  | 6 to 7 | Bypass mode active | uint2 | - | 00b - Normal mode 01b - Bypass mode (Circuit protection is overridden) |
| 3 | 0 to 3 | Qualification Status | uint4 | - | 0 – Unqualified (No AC present) 1 – Unqualified (Bad AC) 2 – Waiting to Qualify 3 – Qualifying 4 – Qualified (Good AC) |

6.1.6 AC Point Status 5

Table 6.1.6a defines the DG attributes, and Table 6.1.6b defines the signal and parameter attributes.

Table 6.1.6a — DG definition

| DG attribute | Value |
| --- | --- |
| Name | AC_STATUS_5 |
| DGN | Defined in device specific definition |
| Default priority | Defined in device specific definition |
| Maximum broadcast gap | Defined in device specific definition |
| Normal broadcast gap | Defined in device specific definition |
| Minimum broadcast gap | 50 ms, see 3.2.4.2 |
| Number of frames | 1 |
| ACK requirements | N/A |

Table 6.1.5b — Signal and parameter definition

| Byte | Bit | Name | Data type | Unit | Value definition |
| --- | --- | --- | --- | --- | --- |
| 0 | - | Instance | uint8 | - | The interpretation depends on the device. |
| 1 | 0 to 1 | Fault - ground voltage | uint2 | - | 00b - No fault 01b - Ground Voltage High |
|  | 2 to 3 | Ground Resistance Out-of-Range Status |  |  | Resistance measurement 00 – Reading good 01 – Reading lower than reported 10 – Reading higher than reported 11 - Data accuracy not available |
| 2 |  | Ground voltage | Uint8 | Vac | see Table 5.3 |
| 4 to 3 |  | Ground resistance | Uint16 | Ω | see Table 5.3 |
| 6 to 5 |  | Ground current (Low Range) | Uint16 | mAac | 0 to 6553.0mA (0.1mA resolution) |

The Ground Resistance Out-of-Range Status field allows devices to provide a meaningful report when the ground resistance is out of the range that the device can measure precisely.  It is used in conjunction with the Ground Resistance field.  If the actual resistance is within the device's measurable range, then the actual value is reported as Ground Resistance and the Out-of-Range status is set to 00b (Reading Good).  If the actual resistance is lower than what the device can measure, then the Ground Resistance is set to the device's lowest measurable value and the Out-of-Range status is set to 01b (Reading lower than reported).   If the actual resistance is higher than what the device can measure, then the Ground Resistance is set to the device's highest measurable value and the Out-of-Range status is set to 10b (Reading higher than reported).  If the Ground resistance value is FFFFh (No data) or FFFEh (Error), the Out-of-Range status is set to 11b (No data)

6.1.6 AC Point Fault Control Status

This is one of two DGs that define the fault control for an AC Point. Table 6.1.6a defines the DG attributes, and Table 6.1.6b defines the signal and parameter attributes.

Table 6.1.6a — DG definition

| DG attribute | Value |
| --- | --- |
| Name | AC_CONFIGURATION_STATUS_1 |
| DGN | Defined in device specific definition |
| Default priority | 6 |
| Maximum broadcast gap | N/A |
| Normal broadcast gap | On Request |
| Minimum broadcast gap | 50 ms, see 3.2.4.2 |
| Number of frames | 1 |
| ACK requirements | N/A |

Table 6.1.6b — Signal and parameter definition

| Byte | Bit | Name | Data Type | Unit | Value definition |
| --- | --- | --- | --- | --- | --- |
| 0 | - | Instance | uint8 | - | The interpretation depends on the device. |
| 1 | - | Extreme low voltage level | uint8 | Vac | see Table 5.3 |
| 2 | - | Low voltage level | uint8 | Vac | see Table 5.3 |
| 3 | - | High voltage level | uint8 | Vac | see Table 5.3 |
| 4 | - | Extreme high voltage level | uint8 | Vac | see Table 5.3 |
| 5 | - | Qualification time | uint8 | s | Time measured in seconds Precision = 1s Max = 0 to 250s |
| 6 | 0 to 1 | Bypass mode | uint2 | - | 00b — Normal Mode 01b — Bypass Mode Circuit Protection is off |

6.1.7 AC Point Fault Control Status 2

This is one of two DGs that define the fault control for an AC Point. Table 6.1.7a defines the DG attributes, and Table 6.1.7b defines the signal and parameter attributes.

Table 6.1.7a — DG definition

| DG attribute | Value |
| --- | --- |
| Name | AC_CONFIGURATION_STATUS_2 |
| DGN | Defined in device specific definition |
| Default priority | 6 |
| Maximum broadcast gap | N/A |
| Normal broadcast gap | On Request |
| Minimum broadcast gap | 50 ms, see 3.2.4.2 |
| Number of frames | 1 |
| ACK requirements | N/A |

Table 6.1.7b — Signal and parameter definition

| Byte | Bit | Name | Data Type | Unit | Value definition |
| --- | --- | --- | --- | --- | --- |
| 0 | - | Instance | uint8 | - | The interpretation depends on the device. |
| 1 | - | High frequency limit | uint8 | Hz | Precision = 1 Hz Value Range = 0 to 250 Hz |
| 2 | - | Low frequency limit | uint8 | Hz | Precision = 1 Hz Value Range = 0 to 250 Hz |
| 4 to 3 |  | Open Ground level | Uint16 | Ω | see Table 5.3 |
| 5 |  | Ground Voltage High level | Uint8 | Vac | see Table 5.3 |

6.1.8 AC Point Fault Control Configuration Command

The format is identical to AC_CONFIG_STATUS_1 and AC_CONFIG_STATUS_2. Note that changing the configuration of one AC Point may affect other AC Points on the same device. The target device should respond with the AC_CONFIG_STATUS for every affected AC Point. Table 6.1.8 defines the DG attributes.

Table 6.1.8 — DG definition

| DG attribute | Value |
| --- | --- |
| Name | ACFAULT_CONFIGURATION_COMMAND_1 ACFAULT_CONFIGURATION_COMMAND_2 |
| DGN | Defined in device specific definition |
| Default priority | 6 |
| Maximum broadcast gap | N/A |
| Normal broadcast gap | N/A |
| Minimum broadcast gap | As needed |
| Number of frames | N/A |
| ACK requirements | ACK/NAK, AC_CONFIG_STATUS_1, AC_CONFIG_STATUS_2 |

6.1.9Alarms

Use calling device alarms.

6.1.10 Test Profiles

The AC_POINT DGs apply to a number of different products, including transfer switches, gensets, inverters, and others. The test profiles apply to these products as well. In this document, the tests have been given the prefix 02, rather than a specific DSA. This is simply a placeholder, and in actual use the tests shall be numbered per the DSA of the device the test is being applied to.

6.1.10.1 Profile 02B-3A: AC Point (Base) Profile

Reporting

| ID | Datum | Test | Required Response | Required Behavior |
| --- | --- | --- | --- | --- |
| 02B-S-01 | AC_STATUS_1 | Instance Voltage Current | The ATS shall broadcast this DGN at least once every 5000 ms. | N/A |

6.1.10.2 Profile 02M-3A: AC Point (Phase Detection Support) Profile

The following profile requirements are in addition to the 02B-3A – AC Point (Base) Profile requirements. Note that the AC_STATUS_1 is included again. This is to indicate that the additional Frequency field is required in the status message.

Reporting

| ID | Datum | Test | Required Response | Required Behavior |
| --- | --- | --- | --- | --- |
| 02M-S-01 | AC_STATUS_1 | Frequency | The ATS shall broadcast this DGN at least once every 5000 ms. | N/A |
| 02M-S-02 | AC_STATUS_3 | Instance Phase Status Complementary Leg | The ATS shall broadcast this DGN at least once every 5000 ms. | N/A |

6.1.10.3 Profile 02C-3A: AC Point (Fault Control Support) Profile

The following profile requirements are in addition to the 02B-3A – AC Point (Base) Profile requirements.

Reporting

| ID | Datum | Test | Required Response | Required Behavior |
| --- | --- | --- | --- | --- |
| 02C-S-02 | AC_STATUS_4 | Instance Voltage Fault Fault – Surge Protection Fault – High Frequency Fault – Low Frequency Bypass Mode Active Qualification Status | The ATS shall broadcast this DGN at least once every 5000 ms. | N/A |

Command Response

| ID | Datum | Test | Required Response | Required Behavior |
| --- | --- | --- | --- | --- |
| 02C-C-01 | ACFAULT_CONFIGURATION_COMMAND_1 | Set AC_CONFIGURATION_STATUS_1 parameters: Arbitrary Parameters | Reports: AC_CONFIGURATION_STATUS_1 immediately with updated parameters from command. | N/A |
| 02C-C-02 | ACFAULT_CONFIGURATION_COMMAND_2 | Set AC_CONFIGURATION_STATUS_2 parameters: Arbitrary Parameters | Reports: AC_CONFIGURATION_STATUS_2 immediately with updated parameters from command. | N/A |
| 02C-C-03 | AC_CONFIGURATION_STATUS_1 | A request for AC_CONFIGURATION_STATUS_1 | Reports: AC_CONFIGURATION_STATUS_1 immediately. | N/A |
| 02C-C-04 | AC_CONFIGURATION_STATUS_2 | A request for AC_CONFIGURATION_STATUS_2 | Reports: AC_CONFIGURATION_STATUS_2 immediately. | N/A |