Please mark all additions in RED and include a Justification.

We are seeing issues with different interpretations of the fan commands between different multiplex suppliers.  In an attempt to provide a solution that works for everyone moving forward, we need add context to reduce the ambiguity in how the commands are interpreted.  Aux Heat (no compressor) + Fan Off is missing -- and has caused issues with both Firefly and ASA.  One assumed Auto meant fan off, the other I'm not sure what they assumed, but they sent Aux Heat + Auto + fan speed not equal to 0, and then didn't understand why the fan was turning on manually.  Logic would state that Auto is automatically figured out: thermostatically or otherwise, which is where all of the confusion is.   I've also got Firefly sending Fan Only Mode + Auto, and they are expecting that to turn off the Fan.  I don't know why then didn't send a mode off instead, but I'm assuming they didn't want to, so I would say Fan Only + Fan Off is desired by them – but I see no way to provide that.   Since this DGN is already not aligned with the data type definitions in table 3.2.3b, where 00b should be OFF, not Auto, we are adding text to try and resolve this another way.

6.16.2 Thermostat Status 1

This communicates user intentions. Table 6.16.2a defines the DG attributes, and Table 6.16.2b defines the signal and parameter attributes. When Aux Heat is implemented, "Heat" refers to heat sources that are integrated with the Air conditioning (e.g. heat strip, heat pump), "Aux Heat" refers to heat sources that are not integrated (e.g. furnace)

Table 6.16.2a — DG definition

| DG attribute | Value |
| --- | --- |
| Name | THERMOSTAT_STATUS_1 |
| DGN | 1FFE2h |
| Default priority | 6 |
| Maximum broadcast gap | 5000 ms |
| Normal broadcast gap | on change and every 2000 ms |
| Minimum broadcast gap | 500 ms |
| Number of frames | 1 |
| ACK requirements | None |

Table 6.16.2b — Signal and parameter definition

| Byte | Bit | Name | Data Type | Unit | Value definition |
| --- | --- | --- | --- | --- | --- |
| 0 | - | Instance | uint8 | - | see Table 5.3 A value of 0 indicates that the fan speed shall be set automatically according to the demand for cooling. A non-zero value indicates that the speed shall be manually overridden. Corresponds to “Zones” in user terminology. |
| 1 | 0 to 3 | Operating mode | uint4 | - | 0000b — Off 0001b — Cool 0010b — Heat 0011b — Auto heat/Cool 0100b — Fan only 0101b — Aux Heat 0110b — Window 0111b – Aux Heat with Fan Off Defrost/Dehumidify |
|  | 4 to 5 | Fan mode | uint2 | - | 00b — Auto1 01b — On2 1 Auto may or may not turn off the fan because it is controlled thermostatically. If Fan Off is desired, an Operating Mode = Off should be sent instead. 2 Note that this is different than the “Fan Only” above. This forces the fan to be on all the time, but allows the heat and cool turn on and off according to the Operating Mode. |
|  | 6 to 7 | Schedule mode | uint2 | - | 00b — Disabled 01b — Enabled If enabled, the set point will change according to a programmed schedule. |
| 2 | - | Fan speed | uint8 | % | see Table 5.3 A value of 0 indicates that the fan speed shall be set automatically according to the demand for cooling. A non-zero value indicates that the speed shall be manually overridden. In the case of Operation Mode = Off, this field shall be ignored. |
| 3 to 4 | - | Setpoint temp – Heat | uint16 | Deg C | see Table 5.3 |
| 5 to 6 | - | Setpoint temp – Cool | uint16 | Deg C | see Table 5.3 |